First:

FIRE PROTECTION SYSTEM DESIGN REPORT

Concept Stage

Al Noor Office Tower

| Document Type | Basis of Design Report (BODR) — FIRE PROTECTION SYSTEM DESIGN REPORT |
| --- | --- |
| Discipline | Fire Fighting (FF) |
| LOD | Concept Design |
| Project | Al Noor Office Tower — Al Noor Development |
| Location | Riyadh, KSA |
| Governing Codes | SBC 801 ¦ SBC 201 ¦ NFPA 13 ¦ NFPA 14 ¦ NFPA 20 |
| Date | 2026-06-11 |
| Revision | R00 — Initial Issue |
| Prepared By | Abdelrhman |

Revision History

| Rev. | Date | Prepared By | Description |
| --- | --- | --- | --- |
| R00 | 2026-06-11 | Abdelrhman | Initial Issue — FIRE PROTECTION SYSTEM DESIGN REPORT Design |

1. Scope of Work

This report establishes the Concept Design basis of the automatic fire protection systems for Al Noor Office Tower, a office building located in Riyadh, KSA comprising 2 floor(s) with a total built-up area of approximately 649 m². The fire protection scope covers the automatic sprinkler system, fire hose cabinets, portable fire extinguishers, standpipe risers, special-hazard aerosol suppression for the electrical/IT rooms, the fire pump set, and the fire water storage tank.

1.1 Governing Codes & Standards

| Code | Application |
| --- | --- |
| SBC 801 (2024) | Saudi Fire Code — fire protection requirements, Civil Defense compliance |
| SBC 201 (2024) | Saudi General Building Code — occupancy classification |
| NFPA 13 (2025 Ed.) | Installation of Sprinkler Systems |
| NFPA 14 (2024 Ed.) | Standpipe and Hose Systems |
| NFPA 20 (2025 Ed.) | Stationary Pumps for Fire Protection |
| NFPA 10 (2026 Ed.) | Portable Fire Extinguishers |
| NFPA 2010 (2025 Ed.) | Fixed Aerosol Fire-Extinguishing Systems — special-hazard rooms |

— Saudi Building Code 2024 editions (in force since 1 July 2025), aligned with the ICC 2021 family.

2. Occupancy & Hazard Classification

2.1 Occupancy Type

The building is classified as Business — Group B.

SBC 201 (2024), §304 — occupancy classification: Business — Group B. [Requirement]

2.2 Hazard Classification (NFPA 13)

| Hazard Class | Spaces | Area (m²) |
| --- | --- | --- |
| Light Hazard | 5 | 529 |
| Ordinary Hazard 1 | 2 | 108 |
| Ordinary Hazard 2 | 1 | 12 |

The governing hazard classification for the hydraulic design is Ordinary Hazard 2.

NFPA 13 (2025), Section 4.3.3.2 — Ordinary Hazard 2 occupancy classification; the governing class is assigned per the contents and heat-release characteristics of the protected spaces. [Requirement]

The following rooms contain energized electrical and electronic equipment for which water-based suppression is not appropriate, and shall be provided with a dedicated Fixed Aerosol Fire-Extinguishing System (special hazard suppression) delivering the required extinguishing concentration upon detection, with full coverage of the protected enclosure volume: Server Room (Ground Floor).

NFPA 2010 (2025), Section 1.1.1 — Scope: "This standard contains the requirements for the design, installation, operation, testing, and maintenance of condensed and dispersed aerosol fire-extinguishing systems for total flooding applications." [Quote]

— Sprinkler heads shown in the schedule for these rooms are Concept-stage placeholders; the final protection scheme (aerosol in lieu of, or supplementary to, sprinklers) shall be confirmed with Civil Defense at detailed design.

3. Sprinkler System — Hydraulic Design

3.1 System Type

A wet pipe automatic sprinkler system shall protect all areas of the building, with pendent sprinklers at ceiling level in finished areas and upright sprinklers in unfinished/exposed areas.

NFPA 13 (2025), Section 3.3 (Definitions) — Wet Pipe Sprinkler System: "A sprinkler system employing automatic sprinklers attached to a piping system containing water and connected to a water supply so that water discharges immediately from sprinklers opened by heat from a fire." [Quote]

SBC 801 (2024), Section 903.3.1.1 — "Where the provisions of this code require that a building or portion thereof be equipped throughout with an automatic sprinkler system in accordance with this section, sprinklers shall be installed throughout in accordance with NFPA 13 except as provided in Sections 903.3.1.1.1 and 903.3.1.1.2." [Quote]

3.2 Design Parameters

| Parameter | Value | Basis |
| --- | --- | --- |
| Design density | 8.1 mm/min (0.20 gpm/ft²) | NFPA 13 (2025) Table 19.2.3.1.1 |
| Design area | 139 m² | NFPA 13 (2025) Table 19.2.3.1.1 |
| Max coverage per sprinkler | 130 ft² (12.1 m²) | NFPA 13 (2025) Table 10.2.4.2.1 |
| Coverage applied | 20.9 m² per sprinkler | Project design value |
| Sprinkler K-factor | K80 (metric) | Project design value |
| Min operating pressure | 52 kPa | Project design value |

NFPA 13 (2025), Section 19.2.3.1.1 and Table 19.2.3.1.1 — Single-Point Design Criteria: for Ordinary Hazard 2 occupancies, the minimum design density is 0.20 gpm/ft² (8.1 mm/min) over 1,500 ft² (139 m²). [Requirement — the density/area curves of pre-2022 editions were replaced by single-point criteria for new systems.]

3.3 Sprinkler Schedule

| Space | Floor | Area (m²) | Hazard | Heads | Branch Ø (mm) | Main Ø (mm) |
| --- | --- | --- | --- | --- | --- | --- |
| Reception & Lobby | Ground Floor | 120 | LH | 6 | 50 | 50 |
| Cafeteria | Ground Floor | 90 | OH1 | 8 | 50 | 50 |
| Toilets — GF | Ground Floor | 28 | LH | 2 | 25 | 25 |
| Server Room | Ground Floor | 18 | OH1 | 2 | 25 | 25 |
| Open Office | Typical Floor | 320 | LH | 16 | 50 | 65 |
| Meeting Room | Typical Floor | 35 | LH | 2 | 25 | 25 |
| Toilets | Typical Floor | 26 | LH | 2 | 25 | 25 |
| Pantry | Typical Floor | 12 | OH2 | 1 | 25 | 25 |
| TOTAL |  |  | OH2 gov. | 39 |  |  |

— Sprinkler counts are area ÷ coverage estimates for Concept stage; final counts and the hydraulically most demanding area shall be confirmed by hydraulic calculation (NFPA 13 Chapter 28) at detailed design.

4. Design Flow Rate & Fire Storage Tank

4.1 Total Design Flow Rate

| Demand component | Flow (L/min) | Flow (gpm) |
| --- | --- | --- |
| Sprinkler demand (density × design area) | 1,126 | 297 |
| Hose stream allowance | 946 | 250 |
| Standpipe demand (NFPA 14) | 1,893 | 500 |
| TOTAL DEMAND | 3,964 | 1,047 |

NFPA 13 (2025), Table 19.2.3.1.2 — hose stream allowance for Ordinary Hazard 2: 250 gpm (combined inside and outside hose), applied in addition to the sprinkler demand. [Requirement]

NFPA 14 (2024), Section 7.10 — minimum standpipe flow: 500 gpm for the hydraulically most remote standpipe plus 250 gpm for each additional standpipe, up to the code maximum. [Requirement]

Selected fire pump: 1,250 gpm @ 3.3 bar (electric + diesel + jockey arrangement), the nearest standard rated capacity above the calculated demand of 1,047 gpm, installed in accordance with NFPA 20 (2025).

SBC 801 (2024), Section 913.1 — where provided, fire pumps shall be installed in accordance with Section 913, SBC 201, and NFPA 20. [Requirement]

— Note: A pump capacity of 1,250 gpm has been applied as a design margin, selecting the nearest standard pump size above the calculated demand of 1,047 gpm. This conservative approach provides system flexibility and ensures compliance under variable demand conditions.

4.2 Fire Storage Tank

| Parameter | Value |
| --- | --- |
| Design duration | 60 min |
| Total demand | 3,964 L/min |
| Tank volume (demand × duration) | 238 m³ |

NFPA 13 (2025), Table 19.2.3.1.2 — minimum water supply duration: Light Hazard — 30 minutes; Ordinary Hazard — 60 to 90 minutes; Extra Hazard — 90 to 120 minutes. [Requirement]

SBC 801 (2024), Section 507.1 — "An approved water supply capable of supplying the required fire flow for fire protection shall be provided to premises upon which facilities, buildings or portions of buildings are hereafter constructed or moved into or within the jurisdiction." [Quote]

5. Fire Hose Cabinets (FHC)

Class II fire hose cabinets (1½ in. / 40 mm hose) shall be distributed so that all portions of each floor are within reach of a hose stream; the Concept-stage estimate is 2 cabinet(s) across 2 floor(s). Cabinets shall be mounted with the valve centreline 1,200–1,500 mm AFF (within the 900–1,500 mm code range).

SBC 801 (2024), Section 905.5 — "Class II standpipe hose connections shall be accessible and shall be located so that all portions of the building are within 30 feet (9144 mm) of a nozzle attached to 100 feet (30 480 mm) of hose." [Quote]

NFPA 14 (2024), Section 7.3.3.1 — Class II systems shall be provided with 1½ in. (40 mm) hose stations located so that all portions of each floor level of the building are within 130 ft (39.7 m) of a hose connection. [Requirement]

NFPA 14 (2024), Section 7.3.1 — hose connections and hose stations shall be located not less than 3 ft (0.9 m) and not more than 5 ft (1.5 m) above the floor, measured to the center of the valve. [Requirement]

6. Portable Fire Extinguishers

Portable fire extinguishers shall be installed throughout the facility in accordance with NFPA 10 and SBC 801 Section 906, complementing the fixed systems above. Concept-stage estimate: 2 extinguisher(s) (Ground Floor: 1 · Typical Floor: 1).

NFPA 10 (2026), Table 6.2.1.1 — for Ordinary (moderate) hazard occupancies: minimum rated single extinguisher 2-A; maximum floor area per unit of A: 1,500 ft² (139 m²); maximum floor area per extinguisher: 11,250 ft² (1,045 m²); maximum travel distance to extinguisher: 75 ft (22.9 m). [Requirement]

NFPA 10 (2026), Section 6.4.1 — "Fire extinguishers with Class C ratings shall be required where energized electrical equipment can be encountered." Applies to electrical and IT/server rooms; the agent shall be electrically nonconductive. [Quote + application]

NFPA 10 (2026), Section 6.1.3.8 — extinguishers with a gross weight not exceeding 40 lb (18.14 kg) shall be installed so that the top is not more than 5 ft (1.53 m) above the floor; clearance between the bottom of the extinguisher and the floor shall be not less than 4 in. (102 mm). [Requirement]

SBC 801 (2024), Section 906.2 — "Portable fire extinguishers shall be selected, installed and maintained in accordance with this section and NFPA 10." [Quote]

7. Pump Room

Location: to be coordinated with the Architectural team. The fire pump room shall provide adequate space and clearance for service, equipment protection, ventilation, and floor drainage, and shall be separated from the remainder of the building by fire-rated construction.

NFPA 20 (2025), Section 4.14.1.1 and Table 4.14.1.1.2 — fire pump units shall be located in rooms separated from the remainder of the building: 2-hour fire-rated construction (or a pump house at least 50 ft / 15.3 m away) in non-sprinklered buildings; 1-hour in fully sprinklered buildings (2-hour for high-rise). [Requirement]

SBC 801 (2024), Section 913.2 — rooms where fire pumps are located shall be separated from all other areas of the building by fire-rated construction in accordance with SBC 201. [Requirement]

8. Design Summary

| Item | Value |
| --- | --- |
| Governing hazard | Ordinary Hazard 2 |
| Total sprinklers (estimate) | 39 heads |
| Design density / area | 8.1 mm/min over 139 m² |
| Total design flow | 3,964 L/min (1,047 gpm) |
| Fire pump (selected) | 1,250 gpm @ 3.3 bar |
| Fire water tank | 238 m³ (60 min) |
| Fire hose cabinets | 2 no. |
| Portable extinguishers | 2 no. |

Second:

HVAC SYSTEM DESIGN REPORT

Concept Stage

Al Noor Office Tower

| Document Type | Basis of Design Report (BODR) — HVAC SYSTEM DESIGN REPORT |
| --- | --- |
| Discipline | Mechanical (HVAC) |
| LOD | Concept Design |
| Project | Al Noor Office Tower — Al Noor Development |
| Location | Riyadh, KSA |
| Governing Codes | SBC 501 ¦ SBC 601 ¦ ASHRAE 62.1 ¦ ASHRAE 90.1 ¦ ASHRAE Handbook — Fundamentals |
| Date | 2026-06-11 |
| Revision | R00 — Initial Issue |
| Prepared By | Abdelrhman |

Revision History

| Rev. | Date | Prepared By | Description |
| --- | --- | --- | --- |
| R00 | 2026-06-11 | Abdelrhman | Initial Issue — HVAC SYSTEM DESIGN REPORT Design |

1. Scope of Work

This report establishes the Concept Design basis of the HVAC systems for Al Noor Office Tower (office, Riyadh, KSA). It covers the cooling load estimation, ventilation (fresh air) strategy, air distribution concept, and main equipment selection for 8 conditioned space(s) totalling 649 m².

1.1 Governing Codes & Standards

| Code | Application |
| --- | --- |
| SBC 501 (2024) | Saudi Mechanical Code — load calculations (§312.1), ventilation (Ch. 4) |
| SBC 601 (2024) | Saudi Energy Conservation Code |
| ASHRAE 62.1 (2025) | Ventilation and Acceptable Indoor Air Quality |
| ASHRAE 90.1 (2025) | Energy Standard — equipment minimum efficiencies |
| ASHRAE Handbook — Fundamentals (2025) | Cooling load methodology (Ch. 18, RTS) |

— Saudi Building Code 2024 editions (in force since 1 July 2025), aligned with the ICC 2021 family.

2. System Selection

Block cooling load: 101.6 kW (28.9 TR); with a diversity factor of 85% the plant duty is 86 kW (24.5 TR). Selected concept: DX splits / VRF — 25 TR total.

ASHRAE 90.1 (2025), Section 6.4.1.1 — mechanical cooling equipment shall meet or exceed the minimum efficiency requirements of the tables of Section 6.8.1 (including the VRF equipment tables, rated per AHRI 1230). [Requirement]

SBC 501 (2024), Section 312.1 — "Heating and cooling system design loads for the purpose of sizing systems, appliances and equipment shall be determined in accordance with the procedures described in the ASHRAE/ACCA Standard 183. Alternatively, design loads shall be determined by an approved equivalent computation procedure, using the design parameters specified in Chapter 3." [Quote]

3. Cooling Load Estimation

3.1 Methodology

Concept-stage loads are computed with a simplified CLTD component method (envelope conduction + solar + infiltration + internal gains + ventilation), applied per space with a 10% safety factor. Detailed loads shall be verified by full energy simulation (HAP) at the detailed design stage.

ASHRAE Handbook — Fundamentals (2025), Chapter 18 — Nonresidential Cooling and Heating Load Calculations: the Radiant Time Series (RTS) method is the recommended procedure for detailed cooling load calculations. [Requirement]

3.2 Design Assumptions

| Parameter | Value |
| --- | --- |
| Outdoor design (cooling) | 45°C DB / 22°C WB (Riyadh) |
| Indoor design | 24°C / 50% RH |
| Wall / Roof U-value | ≤ 0.57 / 0.40 W/m²K |
| Window U / SHGC | 2.8 W/m²K / 0.25 |
| Lighting / Equipment density | 15 / 20 W/m² |
| Infiltration | 0.5 ACH |
| Safety factor / Diversity | 10% / 85% |

3.3 Zone-by-Zone Cooling Load

| Space | Floor | Area (m²) | kW | TR | Supply (L/s) | Fresh Air (L/s) |
| --- | --- | --- | --- | --- | --- | --- |
| Reception & Lobby | Ground Floor | 120 | 18.9 | 5.38 | 1,438 | 126 |
| Cafeteria | Ground Floor | 90 | 26.9 | 7.66 | 1,916 | 320 |
| Toilets — GF | Ground Floor | 28 | 4.3 | 1.22 | 349 | 0 |
| Server Room | Ground Floor | 18 | 3.1 | 0.88 | 257 | 5 |
| Open Office | Typical Floor | 320 | 33.3 | 9.48 | 2,647 | 176 |
| Meeting Room | Typical Floor | 35 | 8.3 | 2.36 | 623 | 56 |
| Toilets | Typical Floor | 26 | 3.9 | 1.12 | 319 | 0 |
| Pantry | Typical Floor | 12 | 2.7 | 0.78 | 222 | 11 |
| TOTAL |  |  | 101.6 | 28.9 | 7,770 | 694 |

— All cooling load values presented in the above schedule represent preliminary estimates appropriate for the Concept Design stage. Final cooling loads, equipment capacities, and system sizing shall be determined through detailed energy simulation using HAP (Hourly Analysis Program) in accordance with the ASHRAE Handbook — Fundamentals (2025), Chapter 18 (RTS method), prior to equipment procurement.

— It should be noted that the preliminary cooling load values presented herein are subject to revision upon completion of the detailed HAP energy simulation. Final calculated loads may deviate from the values indicated above by a margin of up to ±25%, subject to actual building envelope performance, occupancy patterns, and climatic data inputs applied during the detailed design stage.

4. Ventilation (Fresh Air) Strategy

Fresh air quantities are calculated per zone using the ASHRAE 62.1 Ventilation Rate Procedure (Vbz = Rp·Pz + Ra·Az), giving a total outdoor air requirement of 694 L/s.

ASHRAE 62.1 (2025), Section 6.2 (Ventilation Rate Procedure) — the breathing-zone outdoor airflow for each zone shall be calculated as Vbz = Rp·Pz + Ra·Az (Equation 6-1), with the people outdoor air rate (Rp) and area outdoor air rate (Ra) taken from Table 6-1 for the applicable occupancy category of each zone. [Requirement — the per-zone rates applied in this report follow the Table 6-1 occupancy categories listed in the zone schedule.]

SBC 501 (2024), Sections 403.2 and 403.3 with Table 403.3.1.1 — the minimum outdoor airflow rate shall be determined in accordance with Section 403.3, using the occupancy-based ventilation rates of Table 403.3.1.1 (consistent with ASHRAE 62.1). [Requirement]

— Exhaust-governed spaces (mechanical exhaust in lieu of supply OA): Toilets — GF (Exhaust ≥10 ACH) · Toilets (Exhaust ≥10 ACH).

5. Equipment Placement & Coordination

Cooling plant: DX splits / VRF — 25 TR total. Outdoor/plant equipment location: Rooftop — TBC with the Architectural team. Fresh air AHU: Rooftop — TBC. Equipment shall be installed with the manufacturer’s required clearances and on vibration isolators.

SBC 501 (2024), Section 306.5 — mechanical equipment and appliances installed on roofs or elevated structures requiring service shall be provided with a permanent approved means of access. [Requirement]

ASHRAE 62.1 (2025), Section 5.5 and Table 5-1 — outdoor air intakes shall be located so that the separation distance to each contaminant source is not less than the minimum listed in Table 5-1 — e.g., 3 m (10 ft) from toilet/general building exhaust outlets and plumbing vents, and 4.5 m (15 ft) from significantly contaminated exhaust. [Requirement]

6. Design Summary

| Item | Value |
| --- | --- |
| Block cooling load | 101.6 kW (28.9 TR) |
| Plant duty @ diversity | 86 kW (24.5 TR) |
| Selected plant concept | DX splits / VRF — 25 TR total |
| Total supply air | 7,770 L/s |
| Total fresh air (62.1) | 694 L/s |
| Conditioned spaces | 8 |

Third:

PLUMBING & DRAINAGE DESIGN REPORT

Concept Stage

Al Noor Office Tower

| Document Type | Basis of Design Report (BODR) — PLUMBING & DRAINAGE DESIGN REPORT |
| --- | --- |
| Discipline | Plumbing (PL) |
| LOD | Concept Design |
| Project | Al Noor Office Tower — Al Noor Development |
| Location | Riyadh, KSA |
| Governing Codes | SBC 701 ¦ UPC ¦ MEWA / Amanah guidelines |
| Date | 2026-06-11 |
| Revision | R00 — Initial Issue |
| Prepared By | Abdelrhman |

Revision History

| Rev. | Date | Prepared By | Description |
| --- | --- | --- | --- |
| R00 | 2026-06-11 | Abdelrhman | Initial Issue — PLUMBING & DRAINAGE DESIGN REPORT Design |

1. Scope of Work

This report establishes the Concept Design basis of the domestic water supply, drainage, and storm systems for Al Noor Office Tower (office, Riyadh, KSA). It covers the sanitary fixture schedule, water demand and pipe sizing, storage tanks, pump sets, hot water, and the sanitary/storm drainage concept.

1.1 Governing Codes & Standards

| Code | Application |
| --- | --- |
| SBC 701 (2024) | Saudi Plumbing Code — fixtures, water sizing (App. E), drainage |
| UPC (2024 Ed.) | Uniform Plumbing Code — cross-reference where accepted |
| MEWA / Amanah guidelines | Water demand, storage reserve, site drainage |

— Saudi Building Code 2024 editions (in force since 1 July 2025), aligned with the ICC 2021 family.

2. Sanitary Fixture Schedule

| Space | Floor | Water Closet (Tank) | Lavatory / Washbasin | Kitchen Sink | Floor Drain |
| --- | --- | --- | --- | --- | --- |
| Cafeteria | Ground Floor | — | 2 | 2 | 2 |
| Toilets — GF | Ground Floor | 6 | 6 | — | 3 |
| Toilets | Typical Floor | 5 | 5 | — | 2 |
| Pantry | Typical Floor | — | — | 1 | 1 |
| TOTAL |  | 11 | 13 | 3 | 8 |

3. Water Demand Calculation

3.1 Fixture Units (WSFU / DFU)

| Space | Floor | WSFU | DFU | Peak (L/s) | Branch Ø (mm) |
| --- | --- | --- | --- | --- | --- |
| Reception & Lobby | Ground Floor | 0.0 | 0.0 | 0.00 | 0 |
| Cafeteria | Ground Floor | 5.0 | 10.0 | 0.57 | 20 |
| Toilets — GF | Ground Floor | 21.0 | 36.0 | 1.35 | 32 |
| Server Room | Ground Floor | 0.0 | 0.0 | 0.00 | 0 |
| Open Office | Typical Floor | 0.0 | 0.0 | 0.00 | 0 |
| Meeting Room | Typical Floor | 0.0 | 0.0 | 0.00 | 0 |
| Toilets | Typical Floor | 17.5 | 29.0 | 1.21 | 32 |
| Pantry | Typical Floor | 1.5 | 4.0 | 0.25 | 15 |
| TOTAL |  | 45.0 | 79.0 | 2.16 | 40 |

SBC 701 (2024), Section 604 and Appendix E — the water distribution system shall be sized for peak demand using the fixture-unit method: WSFU values are assigned per fixture and the total load is converted to a design flow rate using Hunter’s probability curve, with separate demand curves for flush-tank and flushometer-valve systems. [Requirement]

— Fixture-unit values applied are listed in the project fixture schedule; the demand conversion uses the flush-tank Hunter curve. Where flushometer-valve water closets are adopted, the flushometer demand curve shall be applied at detailed design. Verify the fixture-unit values against the governing code table before issue.

3.2 Peak Flow & Main Sizing

| Parameter | Value |
| --- | --- |
| Total WSFU | 45.0 |
| Peak demand (Hunter) | 2.16 L/s |
| Main supply pipe | 40 mm Ø (PPR) @ 1.72 m/s |
| Max design velocity | 2.0 m/s |
| Min residual pressure | 100 kPa |

3.3 Daily Water Demand

| Parameter | Value |
| --- | --- |
| Occupants | 154 persons |
| Per-capita rate | 45 L/person·day |
| Daily demand | 6.9 m³/day |

— The per-capita consumption rate of 45 L/person/day is a preliminary design value based on established engineering practice for office occupancies in the region — it is not a code-table value and shall be confirmed with the local water authority during detailed design.

4. Water Storage Tanks

| Parameter | Value |
| --- | --- |
| Storage basis | 2 day(s) of daily demand |
| Total storage | 13.9 m³ |
| Underground tank | 11.5 m³ |
| Roof tank | 2.3 m³ (≈ 23 kN full — structural coordination) |

— The 2-day storage basis reflects prevailing municipal-supply reliability practice for KSA — it is a design decision, not a code clause; confirm the required reserve with the local municipality and water authority. Tank locations: TBC — Architectural & Structural coordination.

5. Pumping Systems

| Pump set | Duty | Power |
| --- | --- | --- |
| Booster set (1 duty + 1 standby) | 2.2 L/s @ -2 m | 0.0 kW each |
| Transfer set UG → roof (1+1) | 2.2 L/s @ 23 m | 0.8 kW each |
| Sewage submersible (1+1) | 2.3 L/s @ 6 m | 0.2 kW each |

6. Hot Water

| Parameter | Value |
| --- | --- |
| Hot water daily demand | 1,039 L/day |
| Central heater storage | 420 L |
| Heater capacity | 5.3 kW (8-hour recovery) |
| Hot water peak flow / pipe | 1.03 L/s / 32 mm Ø |

7. Sanitary & Storm Drainage

| Parameter | Value |
| --- | --- |
| Total DFU | 79.0 |
| Main stack | 100 mm Ø |
| Building drain / sewer | 100 mm Ø @ 2% slope |
| Roof rainfall design intensity | 50 mm/hr |
| Roof leaders | 2 × 75 mm Ø (roof area 325 m², 4.5 L/s) |

SBC 701 (2024), Section 710.1 and Table 710.1(1) — the size of the building drain and its branches is determined by the total drainage fixture unit (DFU) load: a 100 mm (4 in.) building drain accommodates up to 180 DFU at 1% slope (1/8 in./ft) and up to 216 DFU at 2% slope (1/4 in./ft). [Requirement]

SBC 701 (2024), Table 704.1 — minimum slope of horizontal drainage piping: 2½ in. (65 mm) and smaller — 1/4 in./ft (2%); 3 in. to 6 in. (80–150 mm) — 1/8 in./ft (1%); 8 in. (200 mm) and larger — 1/16 in./ft (0.5%). [Requirement. Where the UPC governs, UPC (2024) §708.1 requires 2% unless the AHJ approves 1% for 4 in. and larger.]

SBC 701 (2024), Section 704.2 — the size of the drainage piping shall not be reduced in the direction of flow. [Requirement]

8. Design Summary

| Item | Value |
| --- | --- |
| Peak water demand | 2.16 L/s (45.0 WSFU) |
| Main supply pipe | 40 mm Ø PPR |
| Daily demand / storage | 6.9 m³/day / 13.9 m³ (2-day) |
| Tanks (UG + roof) | 11.5 + 2.3 m³ |
| Drainage | 79.0 DFU → 100 mm sewer @ 2% |
| Hot water | 420 L / 5.3 kW |